##### Content From Jira Task – DD-69676

Type: H++ (Complex)

Description: Currently, performance and compliance reports for AER/DEECA are manually compiled. Automation is required for reporting on curtailment (due to export limits, voltage, backstop), total generation, and server performance. Must include customers prior to DERMS implementation.

This requirement introduces automated reporting capability for Flexible Exports (FE), compliance, and operational performance to replace the current manual reporting process used for AER, DEECA, and internal operational monitoring.

The solution must automate the capture, calculation, and production of key FE and inverter-related reports, including operational dashboards, and support both:

customers onboarded to DERMS; and

customers that existed prior to DERMS implementation, where applicable.

Reports:
Inverter Compliance: Tracks inverter compliance over time - AS4777.2 non-conformance, breach of export limit, unauthorised export, export exceeding registered capacity, incl Operational Dashboard
AIO 3.9.6 – AS4777.2(2020) Compliant Inverters

FE Performance: Operational compliance report, incl comparison to service commitment and non-compliance to FE across customers (weekly), incl Operational Dashboard
AIO 3.9.8.1 – Export limit compliance
MO – Service Performance Portal
MO – Test for FE limit enablement

Export Services: FE Export Services Report
AIO 3.9.7.1 – Avg duration full export
AIO 3.9.7.2 – Avg duration no export
AIO 3.9.7.3 – Avg upper limit
AIO 3.9.7.4 – Avg time upper limit unavail

Inverter Curtailment: Tracks customer curtailment - static and flex customers, by voltage, network/backstop event, HC, other etc - also includes total potential generation with no curtailment
AIO 3.9.5.8 – Export customers with measured overvoltage
AIO 3.9.5.9 – Export customers with estimated overvoltage

Dependency: interfaces in R1, req for SEB then extend and dev reports for R2

Data Ingestion Requirements (Interfaces)

The solution shall provide interfaces and data pipelines to ingest, validate and store inverter, DERMS, network and operational data required for flexible exports and solar emergency backstop reporting.

Data Sources

| Dataset | Description | Source | Interface Requirements |
| --- | --- | --- | --- |
| COMPASS Inverter Compliance | COMPASS inverter compliance and issues list. Issues are flagged on a NMI basis, timestamped and with some metadata regarding each particular issue. Of particular interest are the following issues: - UNREGISTERED_EXPORT_DER - EXPORT_LIMIT_EXCEEDED - GENERATION_CAPACITY_LIMIT_EXCEEDED - IES_UNBALANCED_EXPORT - IES_INVERTER_DID_NOT_TRIP - 61000.3.100_HIGH - IES_NIL_VOLT_VAR_RESP_FAILED - IES_VOLT_VAR_RESP_FAILED - IES_VOLT_VAR_RESP_POLARITY - IES_VOLT_WATT_RESP_FAILED Note: COMPASS compliance primarily for legacy devices | COMPASS | Depends on COMPASS extracts; multiple interfaces required to be built; |
| DER Registration Data | Registration data of the DER installation, such as: - Installation Date (Commissioning Date) - Registration Date (Date when Device enrolled to BAU control group) - Capability Test Date, Test and Retry Counts (Installer vs Automatic) - Capability Test Results - Installer - Hardware OEM (Inverter OEM/Model) | DNA / DERMS SF | DD-80808 |
| DER Capability and Settings Data | Capabilities of the connected DER: - PV Capacity, Inverter Capacity (for legacy and DERMS customers data exists in SNET) - DER Configuration Data (Gate Meter Installed etc) (sourced through existing interfaces from DERMS repointed from DnA) | DNA / DERMS | DD-80806 DD-80807 |
| Customer Metadata | Customer metadata such as: - Connected substation, zone substation, feeder - NMI, MeterID, Postcode - Customer Classification (Internal/SNET) - Customer Classification (from CIS) | SNET CIS | SAP CIS to SNET NMI Standing Data Interface Customer |
| DER Controls Data | Historical issued DER controls for each site/device as appropriate (raw data). All available data fields | DNA / DERMS | DD-81075 DD-81170 DD-81171 |
| Timeseries Energy Data | Power Quality Data (5 min timeseries voltage, current, power, reactive power for each phase) Interval Data (Used as fallback for PQ not available or non-AMI customer) 15-30 min timeseries energy consumption data (kWh) | SNET |  |
| MUPS Data | Timeseries Mirror Usage Point Data (MUPS) for each installation: All available data fields | DNA / DERMS | DD-81172 (telemetry data) |
| Export Limit Data | Information and timeseries export limits for each customer: - Static Export Limit (Legacy Customers) - Dynamic Export Limit (Timeseries + Dynamic Flag) - Default/Opt Out (Fixed Static Limit) | DNA / DERMS | DD-81170 |
| Climatic / Weather Data | Postcode level GTI timeseries (15 minute) solar irradiance data from SEB_PRD_APP.DOE_SOLAR_PV Timeseries temperature data per postcode (15 minute) | SNET |  |
| Voltage Data | Binned voltage data per day NETWORK_PRD_DRV.SUB_POWER_QUALITY_DERIVED_DAY | SNET |  |
| MSL Event Data | Start and end times of MSL event. | DERMS | DD-81705 DD-81172 |

Ingestion Functions

The data sources above represent a significant volume of data, therefore the ingestion pipeline should ensure that the data is accurately acquired from the source systems, perform a validation and quality check, store sufficient records for reporting, maintain an auditability of the data and preserve data for both DERMS and pre-DERMS customers where applicable.

Further details TBC

Intermediary Data Tables

The data presented is complex, and translations will be required in order to actually use the data to determine the metrics described in Section 2. There are a few key intermediary data tables that will be required:

Export Limit Data Table

Currently, customers can have a static export limit, or SEB/DERMS export limit (static but with backstop capability), or in future shall have a flexible export limit. The actual export limit that should have been applied at any given time is dependent on several factors:

- The customers’ actual export limit (for static customers)

- The customers’ devices’ connectivity status, and the time since the last connection was made (ramp down behaviour), as well as the inverter’s control response

- Activity of an emergency backstop event (ramp down behaviour)

- The customers’ flexible export limit (for flexible export customers)

- The customer’s default static fallback export limit

- The start date of the customer’s flexible or backstop enabled installation

An interim table is required to translate the requirements above into a usable data structure that shows for any given time interval, a calculated export limit based on the above quantities.

Note: The MRID of each control should be measured against the control response, whether the OEM acknowledges the start and end of the control. If there is no acknowledgement, then we should decide if the device has fallen back to a default limit or is ramping down. This can then be compared to PQ data for dispatch verification.

Other Tables

TBC based on data sources

Derived Metrics and Calculation Requirements

The solution shall calculate intermediary metrics and aggregations that form the basis of regulatory, operational and compliance reporting. This also includes the overlay of business rules on top of the raw datasets and some aggregations to determine compliance status or issues.

Metric Aggregations

All metrics are expected to be calculated at a customer level, typically also at an interval (timeseries) level and aggregated on a regular basis into higher level statistics presented within reports and to the end user via the operational dashboard.

| Time Aggregations | Geographic Aggregations | Electrical Aggregations | General Aggregations |
| --- | --- | --- | --- |
| - Daily - Weekly - Monthly - Yearly | - Postcode - Suburb - Region | - Substation - Feeder - Zone-Substation | - Customer Type (R, C, I, F) - Customer Type (Legacy Static, Static Opt-Out, Flex, SEB) - Has Battery - Has Solar PV - Installer |

Metrics

The following metrics shall be considered.

Note: All business rules are formally yet to be determined.

| Metric Category | Metric | Comment | How? | Used For |
| --- | --- | --- | --- | --- |
| Inverter | Compliance to AS4777.2 (2020) | Tracks the performance of the inverter to AS4777.2 (2020) requirements over time. This metric should have sub-categories related to: - volt-var response - volt-watt responses - inverter disconnection Measured by both alignment to expected response curves at different power levels, and performance over time. | Ingest inverter compliance reports from COMPASS platform to flag customers that require investigation over time. In SNET, perform aggregation and business rules to determine after a certain number of compliance breaches detected in COMPASS, that the customer is non-compliant. | FE AIO |
|  | Breach of Export Limit | Tracks if the customer is exceeding their allocated export limit over time, based on timeseries export limits and power quality data. Measured by quantity, time and power. | Use derived timeseries export limit and customers’ export data to determine for each interval period, if the export limit was breached and by how much. Apply business rules to the data to identify customers that have breached export over 4% for more than 7 consecutive sunny days. Where customers have static export limit (pre-DERMS/FE), then COMPASS datasets may be used to identify and flag customers that need review. | FE SEB AIO |
|  | Unauthorised Export | Tracks customers that are not authorised to export to the network who are doing so, based on timeseries export limits and power quality data. Should be split between customers with registered DER and no registered DER. | Ingest inverter compliance reports from COMPASS platform to flag customers that require investigation. This metric will cover pre-DERMS and DERMS based customers with static and flexible limits. Apply business rules to identify customers with repeated export to the network where no export is permitted. | FE SEB |
|  | Export Exceeding Registered Capacity | Tracks customers with installed DER who are exporting to the network an amount that is greater than the total inverter capacity that is known to be installed at their premises. | Ingest inverter compliance reports from COMPASS platform to flag customers that require investigation. This metric will cover pre-DERMS and DERMS based customers with static and flexible limits. Apply business rules to identify customers who are repeatedly exceeding the inverter capacity recorded. | FE |
| Curtailment | Potential Generation | Total potential generation at Solar Panel DC bus if not limited by any other factors. Measured in kWh or MWh. | This will be an output of Grid Evolution’s SOLACE algorithm. | FE |
|  | Voltage Curtailment | Excessively high voltage causing inverter curtailment. Where voltage is outside a tolerance band, the inverter should ramp down its output according to a pre-defined curve as per AS 4777. | This will be an output of Grid Evolution’s SOLACE algorithm. | FE |
|  | Capacity Curtailment | Curtailment caused by reaching the output rating of the customers inverter. This occurs when there is more available solar generation than the inverter can handle (e.g. a sunny day when solar panels are over-provisioned compared to inverter capacity). | This will be an output of Grid Evolution’s SOLACE algorithm. | FE |
|  | Export Limit Curtailment | Curtailment caused by an applied export limit that was reached. Measured in kWh. | This will be an output of Grid Evolution’s SOLACE algorithm. | FE |
|  | Network Event Curtailment | Curtailment caused by a network event (e.g. MSL event, or sub-transmission trip etc). Measured in kWh. | This will be an output of Grid Evolution’s SOLACE algorithm. | FE |
|  | Hosting Capacity Curtailment | Curtailment of solar exports (when export limit issued) due to limited transformer hosting capacity. Measured in kWh. | Utilise raw hosting capacity dataset in addition to customer’s flexible export limit to determine when the export was limited purely due to hosting capacity issues. Will be dependent on Grid Evolution’s SOLACE algorithm. | FE |
|  | Total Energy Curtailed | Total potential available energy curtailed by any means, measured in kWh. | This will be a summed output of Grid Evolution’s SOLACE algorithm. | FE |
|  | Curtailment Percentage | A measure on a per customer level of the degree to which they are being curtailed, with respect to their system size. | Can be calculated based on static data and outputs of Grid Evolution’s SOLACE algorithm. | FE |
| Export | Service Commitment | Comparison between service level presented to the customer at time of sign up and customers actual export limits over time. | Use timeseries export limit over time and saved service level to calculate a rolling service level and compare to the saved version. May be presented as a percentage or raw figure, pending how best to represent to the customer. | FE |
|  | Duration Full Export | Tracks the duration the customer had access to their “full export” each day. Suggest aggregation of minutes per day. | Use existing Grid Evolution AIO report logic. | FE AIO |
|  | Duration No Export | Tracks the duration the customer had no access to export. Suggest aggregation of minutes per day. | Use existing Grid Evolution AIO report logic. | FE AIO |
|  | Upper Limit | The average “upper limit” that the customer received. Suggest aggregation of the peak value for each day. | Use existing Grid Evolution AIO report logic. | FE |
|  | Time Upper Limit Unavailable | The duration for each customer that the average upper limit was not available. | Combine other metrics into aggregation that calculates when the export limit was above or below the “average upper limit”. Use existing Grid Evolution AIO report logic. | FE |
|  | Service Utilisation | A measure of how much each customer is leveraging any exports they are given. | Compare the assigned export limit, solar data and the customer’s exports to determine to what degree they are using their assigned capacity. | FE |
| Voltage | Measured Overvoltage | Customers that have experienced actual breaches of EDC voltage requirements (>253V), based on measured PQ data. Unit: Count of Customers. | Use PQ data (raw or daily roll up) to flag customers with voltage issues. Only applicable to customers with meters reporting voltage data (PQ meters). | FE AIO |
|  | Estimated Overvoltage | An estimation, across all customers, of those customers who may be experiencing overvoltage day-to-day. Unit: Count of Customers. | This will be an output of Grid Evolution’s SOLACE algorithm. | FE AIO |
|  | Overvoltage Duration | The duration that the customer experienced the overvoltage event throughout the day. Recorded in minutes per day. | Use PQ data (raw) and flagged customers to calculate the part of the day where voltage is greater than 253V. May also consider duration of estimated overvoltage customers. | FE |
| Device | Commissioning Status |  |  | SEB |
|  | Commissioning Report |  |  | SEB |
|  | Device Capacity | How much device capacity is under DERMS control | Sum up total inverter capacity under control of DERMS | SEB |
|  | Device Connectivity 1 | Connectivity status for devices, aggregated by NMI | Current communications status of device(s) | SEB FE |
|  | Device Connectivity 2 | Connectivity status for devices |  |  |
|  | Device Responsiveness |  |  | SEB |
| Operational | Server Availability | Availability of infrastructure over time – split between key systems. | TBC | SEB FE |
|  | Data Completeness | Record any known data issues or dropouts. | TBC | SEB FE |

For some of the metrics above, the tolerance should be configurable and adjustable as required (but audited), and therefore algorithm parameters should reside in a database table with associated history table.

Compliance Mechanisms

Separately to the calculation of metrics to identify non-compliance, where a non-compliance is repeatedly detected, a compliance mechanism is required to record and identify repeat offenders and assets.

The existing compliance implementation is described in Confluence at the link below. This should be used as a basis to build out further compliance mechanisms.

https://ausnetservices-adaptivedelivery.atlassian.net/wiki/spaces/FBPKS/pages/2669674911/Compliance+Implementation

Installer Points System

The backend logic for an installer points system will be required. This should consider the following metrics in determining the compliance for an installation:

- Compliance to AS4777.2 (2020)

- Export Limit Compliance / Unauthorised Export

- Export Exceeding Registered Capacity

- Commissioning Status

Where an installer has multiple consecutive installations over a given time period that fail to meet the compliance requirements above, the installer shall be flagged in the system with a point increase. This should be a dynamic count that is decremented after some time or successful installations, however with history recorded.

The points system should be used to flag regular non-conformers, however no customer/installer should be notified of this as part of DEFE’s current scope of works.

Update Frequency

| Metric | Update Frequency | Data Latency |
| --- | --- | --- |
| All Metrics (not listed below) | Daily at 8am | Within 24 hours |
| SEB – Capacity and Connectivity | Every 30 minutes | Near real-time |
| SEB – Communicating Devices | Every 15 minuets | Near real-time |
| SEB – Timeseries View | Twice Daily | Within 6 hours |

Definition of Non-Conformance/Compliance

TBC

| Metric | Non-Compliant If |
| --- | --- |
| AS4777.2 (2020) | Failure to disconnect from network (at any time) 14 days in which volt-var or volt-watt response has deviated from requirement in standard |
| Export Limit | >4% deviation from export limit on more than 7 consecutive sunny days |
| Unauthorised Export | Export with no registered DER (export above 100W) Export >200W with zero export limit (registered DER) |
| Export Over Registered Capacity | Export occurring >200W above nameplate rating of “export” class inverters installed on site |

Reporting Requirements

There are two types of reporting requirements outlined in this program; formal reports and the operational dashboard.

Formal Reports

Annual Information Order

The AIO is a requirement of the DNSP delivered on a yearly basis, to provide the regulator with information about the DNSP’s network. A specific report for the AIO should be available within the dashboard (extract) or via other extraction means. This should aggregate metrics calculated throughout the year into yearly figures.

The “FE related” aspects of the AIO encompass:

| AIO | Associated Metric | Description |
| --- | --- | --- |
| AIO 3.9.6 | AS4777.2 (2020) Compliant Inverters | Count of compliant inverters on the network. Total for the year. |
| AIO 3.9.8.1 | Export Limit Compliance |  |
| AIO 3.9.7.1 | Average Duration Full Export |  |
| AIO 3.9.7.2 | Average Duration No Export |  |
| AIO 3.9.7.3 | Average Upper Limit | Yearly aggregate, kW, of average upper export limit assigned to customers. |
| AIO 3.9.7.4 | Average Time Upper Limit Unavailable | Yearly aggregate, minutes |
| AIO 3.9.5.8 | Export Customers with Measured Overvoltage | Yearly # customers with measured overvoltage |
| AIO 3.9.5.9 | Export Customers with Estimated Overvoltage | Yearly # customers with estimated overvoltage |

Other

Other formal reports TBC. May be covered by simply selecting appropriate date range on dashboard with an “export” report button.

Dashboards

Dashboard may contain:

- A total compliance metric for the fleet

- A compliance rate over time plot (bar plot, per day or per week, for the selected timeframe)

- An issue type and prevalence plot (horizontal bar plot of compliance area and total count, for the selected timeframe)

- A pie-chart of curtailed devices by the curtailment type (for the selected timeframe – connected, comms failure, network constraint curtailment, voltage curtailment etc)

- Devices in service count

- Plot of telemetry health over time

- Timeseries plot of total allowed export vs total export level

- Timeseries plot of average export vs service commitment

- List of new DERs with an issue over the last X days

- Geographic map of hotspots for non-compliance, or tabulated view with segmentation by network or geographic area

- Statistics divided by “solar inverter”, “battery inverter”, or customer “has solar”, “has battery”

- System availability metric